## 2. ReferenceDocs
Description | The following documents, in whole or in part, are normatively referenced in this document [DIN EN 12831] and are indispensable for its application. For dated references, only the edition cited applies. For undated references, the latest edition of the referenced document (including any amendments) applies.
Identifier | Document Name | ISO
EN ISO 6946 | Building components and building elements — Thermal resistance and thermal transmittance — Calculation method (ISO 6946) | ISO 6946
EN ISO 7345 | Thermal insulation — Physical quantities and definitions (ISO 7345) | ISO 7345
EN ISO 9972 | Thermal performance of buildings — Determination of air permeability of buildings — Fan pressurization method (ISO 9972) | ISO 9972
EN ISO 10077-1 | Thermal performance of windows, doors and shutters — Calculation of thermal transmittance — Part 1: General (ISO 10077-1) | ISO 10077-1
EN ISO 13370 | Thermal performance of buildings — Heat transfer via the ground — Calculation methods (ISO 13370) | ISO 13370
EN ISO 13789 | Thermal performance of buildings — Transmission and ventilation heat transfer coefficients — Calculation method (ISO 13789) | ISO 13789
EN ISO 52000-1 | Energy performance of buildings — Overarching EPB assessment — Part 1: General framework and procedures (ISO 52000-1) | ISO 52000-1

## 3. Terms
ID | Term | Definition | Extra Notes
3.1 | ATD (air terminal device) | air out-/inlets allowing air transfer between external and internal air (external ATD) or between separate rooms (internal ATD) | Note 1 to entry: In the field, the term ATD is used for a broad variety of air out- and inlets. Within this standard, the term refers only to passive devices allowing air flow through a building element (walls, etc.) in a defined manner. It does not include air out-/inlets of fan-assisted ventilation system. Note 2 to entry: Within this standard, it is assumed that external ATDs are only applied in unbalanced ventilation.
3.2 | annual mean external temperature | mean value of the external temperature during the year
3.3 | balanced ventilation | fan-assisted ventilation where the sum of all supply air volume flows equals the sum of all exhausted air volume flows in quantity and over the course of time
3.4 | building element | internal or external component of the building structure and/or thermal envelope or a portion thereof with uniform thermal conditions on each side of the element | EXAMPLE: Wall between two rooms of the same or different temperatures.
3.5 | building entity | certain portion of a building (one or more rooms) used as one unit by one party/occupant, such as: — one apartment / flat; — one office unit… where the heat supply to that unit can be controlled individually by the occupant (usually by means of room temperature control devices) | Note 1 to entry: For the definition of building entities within application of this standard, it is not relevant if the heat supplied to building entities is generated centralized per building or separately in each building entity.
3.6 | design heat load | heat flow (power) required to achieve the specified internal design temperature under external design conditions | Note 1 to entry: The design heat load covers transmission and ventilation heat losses and, if any, an additional heating-up power.
3.7 | design heat loss | heat loss (power) leaving the building to the external environment under specified design conditions
3.8 | design transmission heat loss | heat loss to the exterior and between heated and other heated or unheated spaces inside a building as a result of thermal conduction through the surrounding surfaces | Note 1 to entry: The design transmission heat loss is a portion of the design heat loss.
3.9 | design ventilation heat loss | heat loss to the exterior by ventilation and infiltration through the building envelope and the heat transferred by ventilation from one heated space to another heated or unheated space | Note 1 to entry: The design ventilation heat loss is a portion of the design heat loss.
3.10 | external design temperature | (minimal) external air temperature which is used for the calculation of the design heat losses
3.11 | heated space | space which, per design, is heated to the specified internal design temperature and separated from other spaces by building elements such as walls, etc. | Note 1 to entry: Usually each single (heated) room is considered a heated space.
3.12 | internal air temperature | temperature of the air inside the considered heated space
3.13 | internal design temperature | temperature-value required for the intended use of a heated space and that is used to calculate the design heat loss | Note 1 to entry: The internal design temperature is an operative temperature and, therefore, depends, among other parameters, on the air temperature and the radiant temperature – usually defined in a simplified manner as arithmetic average between both. Note 2 to entry: Default values for the internal design temperature are subject to national regulations.
3.14 | large openings | openings of the enveloping surface of a room/building that are kept open for significant periods over the day on a regular basis; usually, but not necessarily, (large) doors or gates | EXAMPLE: Gates in logistics and industrial halls.
3.15 | mean internal air temperature | mean air temperature of a heated space | Note 1 to entry: With low room heights (h < 4 m), the mean internal air temperature can be assumed to equal the internal design temperature; with larger room heights, the mean internal air temperature is calculated based on the internal design temperature, specifically for the heating system to be used.
3.16 | mean internal surface temperature | mean temperature of a building element’s inner surface | Note 1 to entry: With low room heights (h < 4 m), the mean internal surface temperature can be assumed to equal the internal design temperature; with larger room heights, the mean internal surface temperature is calculated based on the internal design temperature, specifically for the heating system to be used.
3.17 | minimum air change rate | number of air changes per hour that needs to be ensured in order to maintain an appropriate level of air hygiene (reduction of air pollutants, CO2, moisture, etc.), which depends on type of the room (use); subject to national regulation
3.18 | regularly unheated space | space that, by design, is unheated; e.g. unheated attic, unheated corridor, unheated winter garden, etc. | Note 1 to entry: Within this standard, adjacent building entities (neighbouring apartment, etc.) are, for calculational purposes, assumed to be unheated – these, however, do not belong to regularly unheated spaces.
3.19 | unbalanced ventilation | fan-assisted ventilation where the sums of all supply air volume flows and all exhausted air volume flows differ significantly in quantity or over the course of time
3.20 | ventilation | entirety of all processes transporting air, including fan-assisted ventilation by ventilation systems, natural ventilation (“airing”), infiltration through leakages, etc.
3.21 | zone (ventilation zone) | group of rooms that are air-connected by design, either directly or indirectly (through other rooms there between); e.g. through internally mounted air transfer devices / shortened door leafs, etc. | Note 1 to entry: By design, there is no air transfer between ventilation zones. Usually, each building entity is considered a separate zone.

## 4. Symbols&Indexes
Symbol | Name | Unit | Index | Meaning/Use
Φ | Heat power (heat loss, heat load) | W | 50 | Referring to a pressure difference of 50 Pa
H | Heat transfer coefficient | W/K | a | Air
θ | Temperature on the Celsius scale | °C | ann | Annual
U | Thermal transmittance, U-value | W/(m2∙K) | ATD | Air transfer device; refers to externally mounted air transfer devices unless otherwise specified
f | Adjustment/correction factor or term | - | BE | Numbering index for building entitiesa
Δ… | Delta/difference | - | bottom | Referring to the underneath of the building or a portion hereof
A | Area | m2 | build | Building
a, b, c | Calculation parameters | - | comb | Combustion
B’ | Geometric parameter of the floor slab | m | D | Discharge (coefficient)
z | Depth of the floor slab below ground level | m | design | Referring to a design condition or technical property
P | Exposed periphery of the floor slab | m | dir | Direction, orientation
n1…3 | Calculation parameters (exponent) | - | du | Disuse
n | Air change rate | 1/h, h−1 | e | External air, exterior; usually refers to an external design condition
ρ | Density (of air) | kg/m3 | e,m | (Annual) mean external
cp | Specific heat capacity of air (constant pressure) | Wh/(kg∙K) | eff | Effective
q(v) | Air volume flow | m3/h | env | Envelope
q | Specific air permeability of the building envelope | m3/(m2∙h) | equiv | Equivalent (U-value)
V | Volume | m3 | exh | Exhaust
v | Pressure exponent for leakages | - | f | Frame (of a window)
a(ATD…) | ATD authority | - | fac | Facade; vertical external walls
ϕ | Specific heat power | W/m2 | floor | Floor
τ | Building time constant | h | g | Ground
C | Thermal storage capacity | Wh/K | g | Relative to ground level
c | Volume-specific thermal storage capacity | Wh/(m3∙K) | g | Glazing (of a window)
G | Temperature gradient over height | K/m | gain | Heat gains
k | Calculation parameter (factor) | - | GW | Groundwater
h | Height | m | HL | Heat load
d | Thickness | m | hu | Heating-up
λ | Thermal conductivity | W/(m∙K) | i, j | Numbering indices a for heated spaces; where (i) is normally used for heated spaces in consideration and (j) for other heated space interrelating to (i), such as a neighbouring room, etc.
R | Heat transmission resistance | m2K/W | ia | From the considered space (i) to an adjacent (heated) space (a)
Gw | Ground water correction factor | — | iaBE | From the considered space (i) to an adjacent Building entity (aBE)
l | Length (of a linear thermal bridge) | m | iae | From the considered space (i) to the exterior through an adjacent unheated space (ae)
T | Thermodynamic temperature on the Kelvin scale | K | ie | From the considered space (i) to the exterior (e)
v | Wind velocity | m/s | ig | From the considered space (i) to the ground (g)
η | efficiency | - | inf | Infiltration
Ψ | Thermal transmittance of a linear thermal bridge | W/(m∙K) | inf-add | Additional infiltration
|  |  | inner | Inner/internal, Referring to internal dimensions
|  |  | int | Internal; often refers to an internal design condition
|  |  | ix | From the considered space (i) to another space; x being a placeholder for e, a, g, etc.
|  |  | ju | From a space (j) to a space (u) that is looked upon as being unheated, although, design-wise, (u) may be heated or containing heated spaces
|  |  | k | Numbering index a for building elements (walls, windows, ceilings, etc.)
|  |  | l | Numbering index a for linear thermal bridges
|  |  | leak | Leakage(s)
|  |  | m | Numbering index a for punctiform thermal bridges
|  |  | max | Maximum, upper limit
|  |  | measure | Measured or obtained on the basis of a measurement
|  |  | min | Minimum, lower limit
|  |  | occup | Occupied; referring to the occupied zone as the height level that internal design conditions shall be achieved for
|  |  | open | Openings (e.g. open gates)
|  |  | p | Constant pressure
|  |  | rad | Radiant
|  |  | rec | Heat recovery
|  |  | Ref | Reference site
|  |  | sb | Setback
|  |  | shield | Shielding
|  |  | si, se | Internal and external heat transmission (e.g.: internal air to building element, building element to external air)
|  |  | small_open | Small openings
|  |  | sup | Supply air
|  |  | surf | Surface
|  |  | T | (Heat) Transmission
|  |  | TB | Thermal bridge
|  |  | techn | Technical, technically required or caused
|  |  | th | Thermally induced
|  |  | total | Total, overall
|  |  | transfer | Referring to air volume flows between rooms
|  |  | u | Referring to a space (u) that is looked upon as being unheated although, design-wise, (u) may be a heated space or an entity containing heated spaces
|  |  | U | Referring to a quality or condition regarding the thermal transmittance (U-value)
|  |  | ue | From a space (u) that is looked upon as being unheated to the exterior (e)
|  |  | v | Volume or volume flow
|  |  | V | Ventilation
|  |  | w | Wind-induced
|  |  | z | Numbering index for (ventilation) zones

## 5. Calc Methods
# | Method | Application | Restrictions within the overall scope of this standard
1 | Standard method – Heat load of rooms, building entities and buildings (6) | — Versatile approach for any consideration on heat losses/load in accordance with Clause 1 (Scope) — Typically, dimensioning of components of heating systems in — new buildings — extensive reconstruction measures | -
2 | Simplified method for the calculation of the design heat load of a heated space (single rooms) (7) a | Determination of room heat load prior to measures concerning the heat emission system in single rooms — exchange of heat emission (e.g. radiators) — hydraulic balancing | a) Only applicable to rooms in: 1) residential buildings or buildings of similar use 2) existing buildings / building stock 3) buildings with natural ventilation
3 | Simplified method for the calculation of the building design heat load (8) a | Determination of building heat load prior to measures concerning the heat generation, e.g. — exchange of the heat generator
a The simplified methods (7, 8) are not suited to substitute the standard method (6) in case of extensive measures concerning heat generation AND emission.

## 6. Standard Method
transmission heat losses to exterior
ventilation heat loss of the building
additional heating-up power | only those heating-up powers may be taken into account that can be assumed to occur at the same time and under external design conditions – it is strongly recommended that the consideration of heating-up power in the sizing of heat generators is explicitly agreed upon between the customer and the contractor sizing/installing the heat generator
Output Data
Description | Symbol | Unit | Intended use | Intended destination module | Python variable name
Design heat load of a heated space | ΦHL,i | W | — Dimensioning of components for heat emission and distribution — application of the results in the field (see Intended use) |  | heatLoadSpace
Design heat load of a building entity | ΦHL,BE | W | — Dimensioning of heat generators — Input value for the determination of heat generation losses — application of the results in the field (see Intended use) | — possible application in M3–2 (energy needs), M3–4 (energy efficiency) and where the power of a heat generation system may be required as input | heatLoadBE
Design heat load of a building | ΦHL,build | W |  |  | heatLoadBuild
Input Data
Symbol | Description | Unit | Source (highest to lowest priority) | Python variable name
Aenv,i | Envelope of a heated space (i); surface area of all building elements (k) of a heated space (i) in contact with external air or unheated spaces. Aenv can be based on internal or external dimensions. If known, Aenv shall refer to the same dimension specifications as the air permeability at 50 Pa that is determined by means of an air-tightness test or taken from national default values. Where dimension specifications are unknown, Aenv shall refer to external dimensions. Reference to external dimensions is always acceptable (conservative estimate). | m2 | — Building data, measurement | A__env_i
Aenv,build | Envelope of a building (build); surface area of all building elements (k) of a building (build) in contact with external air or unheated spaces. Aenv can be based on internal or external dimensions. If known, Aenv shall refer to the same dimension specifications as the air permeability at 50 Pa that is determined by means of an air-tightness test or taken from national default values. Where dimension specifications are unknown, Aenv shall refer to external dimensions. Reference to external dimensions is always acceptable (conservative estimate). | m2 | — Building data, measurement | A__env_build
Aenv,z | Envelope of the zone (z); surface area of all building elements (k) of a ventilation zone (z) in contact with external air or unheated spaces. Aenv can be based on internal or external dimensions. If known, Aenv shall refer to the same dimension specifications as the air permeability at 50 Pa that is determined by means of an air-tightness test or taken from national default values. Where dimension specifications are unknown, Aenv shall refer to external dimensions. Reference to external dimensions is always acceptable (conservative estimate). | m2 | — Building data, measurement | A__env_z
Ak | Area of the building element (k); can be based on internal or external dimensions depending on context, as follows — Calculation of transmission heat transfer coefficients: Ak shall refer to the same dimension specifications as the U-values applied — Calculation of envelope surfaces in the context of ventilation heat losses: Ak shall refer to the same dimension specifications as the air permeability at 50 Pa that is determined by means of an air-tightness test or taken from national default values. Where dimension specifications are unknown, Ak shall refer to external dimensions. Reference to external dimensions is always acceptable (conservative estimate). | m2 | — Building data, measurement | A__k
ceff | Volume-specific thermal storage capacity of the building | Wh/(m3∙K) | — Building data — National annex to this standard in accordance with Subclause A.2.7 — Subclause B.2.7 | c__eff
cp | Specific heat capacity of air at constant pressure | Wh/(kg∙K) | — Building data, design, ventilation concept — National annex to this standard in accordance with Subclause A.2.8 — Subclause B.2.8 | c__p
fU,k | Correction factor for the influence of building part properties and meteorological conditions not taken into account in the calculation of U-values | - | — National annex to this standard in accordance with Subclause A.2.2 — Subclause B.2.2 | f__U_k
fqv,z | Volume flow factor of the zone (z); optional: not required in naturally ventilated air-tight zones without ATDs | - | — National annex to this standard in accordance with Subclause A.2.12 — Subclause B.2.12 | f__qv_z
fdir,z | Factor for the orientation of zone (z) | - | — National annex to this standard in accordance with Subclause x A.2.15 — Subclause B.2.15 | f__dir_z
fi-z | Ratio between the minimum air volume flows of single rooms (i) being part of the zone (z) qv,min,i and the resulting air volume flow of the entire zone (z) | - | — National annex to this standard in accordance with Subclause A.2.9 — Subclause B.2.9 | f__i_z
ffac,z | Adjustment factor for the number of exposed facades of the zone (z) in accordance with EN ISO 13789; optional: only required in zones with unbalanced ventilation | - | — National annex to this standard in accordance with Subclause A.2.16 — Subclause B.2.16 | f__fac_z
fθann | Correction factor taking into account the annual variation of the external temperature | - | — National annex to this standard in accordance with Subclause A.2.3 — Subclause B.2.3 | f__theta_ann
Gθ,Ref | Temperature gradient of the reference site; a positive value stands for increasing temperature with increasing height | K/m | — National annex to this standard in accordance with Subclause A.4.1; no informative default values provided by this standard | G__theta_Ref
hBuild | Mean height of the building above sea level | m | — Building data / data on building site | h__Build
hRef | Mean height of the reference site (e.g. a state or a certain region) above sea level | m | — National annex to this standard in accordance with Subclause A.4.1; no informative default values provided by this standard | h__Ref
hi | Mean internal height of the room (i); only required in with large ceiling heights (≥4 m) | m | — Building data, measurement | h__i
hoccup,i | Height of the occupied zone of the room (i); only required in with large ceiling heights (≥4 m) | m | — National annex to this standard in accordance with Subclause A.2.6 — Subclause B.2.6 | h__occup_i
kΤ | Slope; parameter for the adjustment of the external design temperature taking into account the influence of the building time constant on heat loss | K/h | — National annex to this standard in accordance with Subclause A.4.1 — Subclause B.4.1 | k__Tau
nmin,i | Minimum air change rate of the considered heated space (i), required for reasons of air quality / hygiene and comfort | h−1 | — Building data → design / ventilation concept — National annex to this standard in accordance with Subclause A.2.11 — Informative Subclause B.2.11 | n__min_i
qenv,50 (n50) | Air permeability (alternatively, air change rate) at a pressure difference of 50 Pa (ATDs, if any, closed); considered a building property | m3/(m2∙h) (h−1) | — Building data, design, ventilation concept, air-tightness measurement (EN ISO 9972) — National annex to this standard in accordance with Subclause A.2.10 — Subclause B.2.10 | q__env_50_n50
qv,ATD,design,i | Design air volume flow of the ATDs in room (i); optional: only required with ATDs | m3/h | — Building data, design, ventilation concept — National annex to this standard in accordance with Subclause A.2.13 — Subclause B.2.13 | q__v_ATD_design_i
qv,ATD,design,z | Design air volume flow of the ATDs in zone (z); optional: only required with ATDs | m3/h | — Building data, design, ventilation concept — National annex to this standard in accordance with Subclause A.2.13 — Subclause B.2.13 | q__v_ATD_design_z
qv,comb,i | Air volume flow exhausted from the heated space (i) that, in case of a ventilation system, has not been included in the exhaust air volume flow qv,exh,i of the ventilation system – typically, but not necessarily for combustion air; optional: only required if there is such a technical system (e.g. open flue heaters) | m3/h | — Building data, design, ventilation concept | q__v_comb_i
qv,exh,i | Exhaust air volume flow from the heated space (i); optional: only required in ventilation systems with exhaust air | m3/h | — Building data, design, ventilation concept | q__v_exh_i
qv,open,i | External air volume flow into the heated space (i) through large openings; optional: only required if large openings are to be considered | m3/h | — Building data, design, ventilation concept — National annex to this standard in accordance with Subclause A.2.17 — Subclause B.2.17 | q__v_open_i
qv,sup,i | Supply air volume flow into the heated space (i); optional: only required in ventilation systems with supply air | m3/h | — Building data, design, ventilation concept | q__v_sup_i
qv,transfer,ij | Transfer air volume flow into the heated space (i); optional: only required in spaces with internal air transfer from one space to another | m3/h | — Building data, design, ventilation concept | q__v_transfer_ij
Uequiv,k | Equivalent thermal transmittance of a building element (k) in contact with the ground (g) | W/(m2∙K) | — National annex to this standard in accordance with Subclause A.2.3 — Subclause B.2.3 / Annex E | U__equiv_k
Uk | Thermal transmittance of the building element (k), determined in accordance with: EN ISO 6946 (opaque elements) EN ISO 10077-1 (doors and windows) information given in European Technical Approvals | W/(m2∙K) | — Building data — National annex to this standard in accordance with Subclause A.4.3 — Subclause B.4.3 | U__k
Vi | Internal volume of the considered heated space (i) | m3 | — Building data / Measurement | V__i
Ve | External building volume | m3 | — Building data / Measurement | V__e
vleak,z | Pressure exponent of zone (z); optional: only required in zones with ATDs | - | — National annex to this standard in accordance with Subclause A.2.14 — Subclause B.2.14 | v__leak_z
ΔpATD,design,z | Design pressure difference of the ATDs in zone (z); optional: only required in zones with ATDs | Pa | — Building data, design, ventilation concept — National annex to this standard in accordance with Subclause A.2.13 — Subclause B.2.13 | delta__p_ATD_design_z
ΔUTB | Blanket additional thermal transmittance for thermal bridges. ΔUTB incorporates thermal bridges in a simplified manner; where a more detailed consideration of thermal bridges is required, the method described in Annex E may be used instead if not overridden by national specifications to this standard | W/(m2∙K) | — National annex to this standard in accordance with Subclause A.2.1 — Subclause B.2.1 | delta__U_TB
Δθe,Τ,0 | Basic value; parameter for the adjustment of the external design temperature taking into account the influence of the building time constant on heat loss | K | — National annex to this standard in accordance with Subclause A.4.1 — Subclause B.4.1 | delta__theta_e_Tau_0
Δθe,Τ,max | Upper limit; parameter for the adjustment of the external design temperature taking into account the influence of the building time constant on heat loss | K | — National annex to this standard in accordance with Subclause A.4.1 — Subclause B.4.1 | delta__theta_e_Tau_max
Δθe,Τ,min | Lower limit; parameter for the adjustment of the external design temperature taking into account the influence of the building time constant on heat loss | K | — National annex to this standard in accordance with Subclause A.4.1 — Subclause B.4.1 | delta__theta_e_Tau_min
ηrec,z | Efficiency of the heat recovery assigned to zone (z); refers to design external conditions*; optional: only required in case of ventilation systems with heat recovery. * Example: If, for a given ventilation system, heat recovery is typically bypassed under design external conditions, ηrec,z = 0 | - | — Building data, design, ventilation concept | eta__rec_z
Φgain,i | Heat gains (power) for the room (i) that occur under design external conditions | W | — National annex to this standard in accordance with Subclause A.2.19 — Subclause B.2.19 | Phi__gain_i
ϕhu,i | Specific additional power for heating up after temperature setback for the room (i) | W/m2 | — National annex to this standard in accordance with Subclause A.2.18 — Subclause B.2.18 / Annex F | phi__hu_i
θe,m | Annual mean external temperature | °C | — National annex to this standard in accordance with Subclause A.4.1; no informative default values provided by this standard | theta__e_m
θe,Ref | External design temperature of the reference site | °C | — National annex to this standard in accordance with Subclause A.4.1; no informative default values provided by this standard | theta__e_Ref
θexh,z | Temperature of the exhaust volume air flow from the zone (z); optional: only required in ventilation systems with exhaust air | °C | — Building data, design, ventilation concept — Estimation based on per-room values (Subclause 6.3.3.7, Formula (38)) | theta__exh_z
θint,i | Internal design temperature of the considered heated space (i). Depending on context, other numbering indices than (i) may be used | °C | — Building data, design — National annex to this standard in accordance with Subclause A.4.2 — Subclause B.4.2 | theta__int_i
θtransfer,ij | Temperature of the transfer air volume flow into the heated space (i) from another space (j); optional: only required in spaces with internal air transfer from one space to another. | °C | Room height < 4 m: θtransfer,ij = θint,j see θint,i, Room height ≥ 4 m: θtransfer,ij = θ*int,j see θ*int,i | theta__transfer_ij
θrec,z | Temperature of the supply air volume flow into zone (z) after passing heat recovery, but without “active” preheating; optional: only required in ventilation systems with exhaust and supply air | °C | — Building data, design, ventilation concept — Subclause 6.3.3.7, Formula (37) | theta__rec_z
θ*int,k | Mean internal surface temperature of a building element (k) | °C | Room height < 4 m: θ*int,k = θint,i see θint,i, Room height ≥ 4 m: Subclause 6.3.8.2 | theta_star__int_k
θ*int,i | Mean internal air temperature of a room (i) | °C | Room height < 4 m: θ*int,i = θint,i see θint,I Room height ≥ 4 m: Subclause 6.3.8.3 | theta_star__int_i
θu | Temperature of an adjacent building entity that is looked upon as being unheated although it may contain rooms that, by design, are heated | °C | — National annex to this standard in accordance with Subclause A.2.5 — Subclause B.2.5 / Annex D | theta__u
ρ | Density of air | m3/kg | — Building data, design, ventilation concept — National annex to this standard in accordance with Subclause A.2.8 — Subclause B.2.8 | rho

## 7
Symbol | Description | Unit | Source
Ak | Area of the building element (k) | m2 | — Building data / Measurement
fint-ext | ratio between external and internal surface areas | - | — Building data, if any; — National annex to this standard in accordance with Subclause A.3.1; — Subclause B.3.1
Uk | Thermal transmittance of the building element (k) | W/(m2∙K) | — Building data; — National annex to this standard in accordance with Subclause A.4.3; — Subclause B.4.3
ΔUTB | Blanket additional thermal transmittance for thermal bridges | W/(m2∙K) | — National annex to this standard in accordance with Subclause A.3.2; alternatively A.2.1; — Subclause B.3.2; alternatively B.2.1
Vi | Internal volume of the considered heated space (i) | m3 | — Building data / Measurement
ni | Air change rate of the considered heated space (i) | h−1 | — Building data; — National annex to this standard in accordance with Subclause A.3.4; — Subclause B.3.4
θint,i | Internal design temperature of the considered heated space (i) | °C | — Building data, design; — National annex to this standard in accordance with Subclause A.4.2; — Subclause B.4.2
θe | External design temperature | °C | — National annex to this standard in accordance with Subclause A.4.1a aWithin this simplified approach, θe = θe, Ref.
fx | Temperature correction factor | - | — National annex to this standard in accordance with Subclause A.3.3; alternatively A.2.4 (→f1); — Subclause B.3.3; alternatively B.2.4 (→f1)

## 8
Symbol | Description | Unit | Python Variable Name | Required Input | Input notes | Source
Ak | Area of the building element (k) | m2 | a__k | a__k | can't be <= 0 | — Building data / Measurement
Uk | Thermal transmittance of the building element (k) | W/(m2∙K) | u__k | u__k OR build_year, building_element_type, building_element_sub_type | as no data is available for Annex A, using default values from Annex B. This means that build year and building_element_type (e.g. "Roller shutters") and building_element_sub_type (e.g. "new, insulated") are required inputs. See table below | — Building data — National annex to this standard in accordance with Subclause A.4.3 — Subclause B.4.3
ΔUTB | Blanket additional thermal transmittance for thermal bridges | W/(m2∙K) | delta__utb | delta__utb OR selection_criteria | no data from A; using B, which provides default values (Annex C can be used too, but seems to overcomplicate things, for now). This means that selection_criteria is required input. See table below | — National annex to this standard in accordance with Subclause A.3.2; alternatively A.2.1 — Subclause B.3.2; alternatively B.2.1
VBuild | Internal volume of the considered heated building | m3 | v__build | v__build | can't be <= 0 | — Building data / Measurement
nBuild | Air change rate of the considered heated building | h−1 | n__build | n__build OR build_year OR air_tightness_level | no data from A; using Table B.12. required input: year of construction or additionally air tightness level to override year of construction. See table below This one could have some confusion, as the table gives h-1 values as well as building years and building tightness levels (obvious leakages vs. tight windows). I have interpreted it as following: 1. tightness level takes precedence 2. if no tightness level is given, use the year of construction | — Building data — National annex to this standard in accordance with Subclause A.3.4 — Subclause B.3.4
θint,build | Internal design temperature of the considered heated building | °C | theta__int_build | theta__int_build OR building_type | no data from A; using Table B.14 required input: internal design temperature. If that is not provided, building type must be provided. See table below | — Building data, design — National annex to this standard in accordance with Subclause A.4.2 — Subclause B.4.2
θe | External design temperature | °C | theta__e | theta__e | Nationally provided values of the external design temperature θe,Ref shall be determined in accordance with national regulation, e.g. after EN ISO 15927-5. This will have to be provided from the source; I am not currently calculating this | — National annex to this standard in accordance with Subclause A.4.1a aWithin this simplified approach, θe = θe, Ref.
fx | Temperature correction factor | - | f__x | f__X OR be_adjacent_to | no data from A; Table B.2 from annex B.2.4 is available, but the simpler version is from B.3.3. For the simplified calculation I will use B.3.3. required input: BE adjacent to. See table below | — National annex to this standard in accordance with Subclause A.3.3; alternatively A.2.4 (→f1) — Subclause B.3.3; alternatively B.2.4 (→f1)
Thermal Transmittance, Uk
be_type | be_sub_type
Windows, French doors | 'Wooden frame, single glazing', 'Wooden frame, double glazing', 'Wooden frame, insulation glazing', 'Plastic frame, insulating glazing', 'Metal frame, insulating glazing'
Roller shutters | 'old, non-insulated' 'new, insulated'
Doors | 'all'
External walls, walls against ground, internal walls against unheated cellars | 'Solid construction (masonry, concrete or similar)', 'Wooden construction (timber frame construction, prefabricated house or similar)'
Ceilings against ground or unheated cellars | 'Solid construction (masonry, concrete or similar)', 'Wooden beam ceiling'
Roofs and walls between heated and unheated attics | 'Solid construction', 'Wooden construction'
Top storey ceilings and ceilings above ambient (passageways, etc.) | 'Solid', 'Wooden beam ceiling'
Thermal Transmittance for thermal bridges ΔUTB
Selection criteria
New buildings with a high level of heat insulation and attested minimization of thermal bridges that exceeds generally recognized rules of practice
New buildings in compliance with generally recognized rules of practice regarding the minimization of thermal bridges
Buildings with mainly internal heat insulation broken by solid ceilings (e.g. reinforced concrete)
All other buildings
Air change rate nBuild
Air tightness level
buildings with tight windows
buildings with obvious leakages
Internal design temperature
Building type
Single office
Landscaped office
Conference room
Auditorium
Cafeteria/Restaurant
Classroom
Nursery
Department store
Residential
Bathroom
Church
Museum/Gallery
Temperature adjustment term f1 (heat loss to unheated spaces and ceiling heights < 4 m)
Unheated space type | Sub-type | f1
Room or group of adjoining rooms/spaces | 1 external wall | 0.4
Room or group of adjoining rooms/spaces | 2 external walls without external doors | 0.5
Room or group of adjoining rooms/spaces | 2 external walls with external doors | 0.6
Room or group of adjoining rooms/spaces | 3 or more external walls | 0.8
Basement | without external doors/windows | 0.5
Basement | with external doors/windows | 0.8
Roof space | high ventilation rate of the roof space | 1
Roof space | other non-insulated roofs | 0.9
Roof space | insulated roofs | 0.7
Circulation area | internal space (no external walls) with low ventilation (≤0.5 h−1) | 0
Circulation area | freely ventilated | 1
Floor | suspended (floor above crawl space) | 0.8
Temperature adjustment term f1 (heat loss to unheated spaces)
Building elements adjacent to | Correction factor fx | Index
external air | 1 | ie
unheated spaces or another building entity | 0.5 | iu
ground | 0.3 | ig
heated space | 0.3 | ij

## Sheet9
6.3.2 Design transmission heat losses of a heated space (i) Total design transmission heat loss ΦT,i | Φ_T,i=(H_T,ie+H_T,ia+H_T,iae+H_T,iaBE+H_T,ig)⋅(θ_int,i−θ_e) | Where: - ΦT,i is the Total Design transmission heat loss of the heated space (i) in W. - HT,ix denotes the transmission heat transfer coefficient from the heated space (i) to another space (x), which can be: - HT,ie directly to the exterior (e) - HT,ia to adjacent heated spaces (a) - HT,iae to the exterior through unheated spaces and neighbouring building entities (ae) - HT,iaBE to adjacent building entities (aBE) - HT,ig to the ground - θint,i represents the internal design temperature in °C. - θe is the external design temperature in °C.
6.3.2.2 Heat transfer coefficient directly to the exterior, HT,ie | H_Tie​=(∑​A_k⋅(​U_k​+ΔU_TB​)⋅f_U,k​⋅f_ie,k) | Where: - HTie: Transmission heat transfer coefficient from the heated space (i) to the exterior (e) in W/K - Ak: Surface area of the building element (k) in m^2 - Uk: Thermal transmittance of the building element (k) in W/(m^2∙K) - ΔUTB: Blanket additional thermal transmittance for thermal bridges in W/(m^2∙K). It's 0 for specific cases. - fU,k ​ : Correction factor for certain influences. Dimensionless. - fie,k: Temperature adjustment factor. Dimensionless.

## Design
Consideration
which calculation method to use
which variables are pre-populated/come from documentation
which variables come from user
which variables come from other sources
room height >4m

## Notes
Note
rooms of height over 4m are treated differently; possible variable required
simplified methods can be applied given certain boundary conditions; possible variable required
initially, I assume simplified methods, as the general method is extremely complex. Simplified methods apply to existing residential buildings with natural ventilation

## Q's
Question | Answer
simplified methods (ch5) "are not suited to substitute the standard method (6) in case of extensive measures concerning heat generation AND emission." - do heat pumps influence both generation and emission? (presumably yes)
what is meant by "envelope", e.g. of a heated space? | boundary that separates a heated space from unheated spaces or the outside environment. This typically includes the walls, floors, ceilings, windows, and doors that enclose a particular space. The envelope plays a crucial role in insulating the space and preventing heat loss, making its design and materials important for energy efficiency